## Tabelle1
				Holding Registers					Input Registers
Reg Nr	GrowattSpecVarName	Our Variable Name	Bedeutung	Writable	16.01.2024 19.40	17.01.24 14:23	28.11.2024 19.30	01.12.2024 15.04		GrowattSpecVarName	Our Variable Name	Bedeutung	16.01.2024 19.40	17.01.24 14:23	28.11.2024 19.30	01.12.2024 15.04
0			On/Off The Standby On/Off / state and the AC / output DisEN/EN / state; The low byte is / the Standby / on/off(1/0), the high / byte is the AC output / disable/enable (1/0). 0x0000: Output enable; / 0x0100: Output disable;		0	0	0	0	0	System Status	inverterStatus	System running Status: 0: Standby; / 1;PV an Grid Combine Discharge / 2: Discharge; / 3: Fault; / 4: Flash; / 5: PV charge; / 6: AC charge; / 7: Combine charge; / 8: Combine charge / and Bypass; / 9: PV charge and / Bypass; / 10: AC charge and Bypass; / 11: Bypass; / 12: PV charge and / Discharge;	2	12	2	12
1			OutputConfig AC output set 0: BAT First; 1: PV First; 2: UTI First; 3: PV&UTI First	Writable	0	0	0	0	1	Vpv1	vpv1	Vpv1 PV1 Voltage now (0.1V)	0	2589	0	1358
2			ChargeConfig Charge source set 0: PV first; 1: PV&UTI; 2: PV Only;	Writable	0	0	0	0	2	Vpv2	vpv2	Vpv2	0	0	0	0
3			UtiOutStart Hour 0-23	Writable	0	0	0	0	3	Ppv1 High Byte	ppv1	Ppv1 H PV1 charge power (high) High Byte	0	0	0	0
4			UtiOutEnd Hour 0-23	Writable	0	0	0	0	4	Ppv1 Low Byte	ppv1	PV1 charge power (low) (0.1W)	0	1640	0	3000
5			Utility charge Start, Hour 0-23	Writable	16	16	16	16	5	Ppv2 High Byte	ppv2	Ppv2 H	0	0	0	0
6			UtiChargeEnd Hour 0-23	Writable	0	0	4	4	6	Ppv2 Low Byte	ppv2	Ppv2 L	0	0	0	0
7			PVModel PV Input Mode 0:Independent; 1: Parallel;	Writable	0	0	0	0	7	Buck1Curr	buck1curr	Buck1Curr Buck1 current (0.1 A) Current to Battery now	0	31	0	56
8			AC Input Mode: 0-APL,90-280VAC 1-UPS, 170-280VAC, 2-GEN	Writable	1	1	1	1	8	Buck2Curr		Buck2Curr	0	0	0	0
9			Firmware version H ASCII 6		12342	12342	12342	12342	9			OP_Watt H Output active power (high)	0	0	0	0
10			Firmware version M ASCII .		14126	14126	14126	14126	10			OP_Watt L Output active power (low) (0.1 Watt)	100	110	0	5150
11			Firmware version L ASCII 4		17972	17972	17972	17972	11			OP_VA H Output apparent power (high)	0	0	0	0
12			Firmware version2 H ASCII 6		12342	12342	12342	12342	12			OP_VA L Output apparent power (low) (0.1VA)	1400	890	1150	5400
13			Firmware version2 M ASCII .		14382	14382	14382	14382	13			ACChr_Watt H	0	0	0	0
14			Firmware version2 L ASCII 4		17972	17972	17972	17972	14			ACChr_Watt L AC charge watt (low) 0.1 Watt	0	0	0	0
15			LCD language 0-1 1-english	Writable	0	0	0	0	15			ACChr_VA H AC charge apparent power / (high) 0.1VA	0	0	0	0
16			?		0	0	0	0	16			ACChr_VA L AC charge apparent power / (low) 0.1 VA	0	0	0	0
17			?		0	0	0	0	17			Bat Volt 0.1V	5232	5275	5320	5297
18			Output Volt Type 0: 208VAC; / 1: 230VAC 2: 240VAC 3:220VAC 4:100VAC 5:110VAC 6:120VAC	Writable	1	1	1	1	18	BatterySOC	soc	BatterySOC 0-100%	48	50	76	97
19			OutputFreqType 0: 50Hz; 1: 60Hz	Writable	0	0	0	0	19			Bus Voltage	4143	4272	4213	4180
20			OverLoadRestart 0:Yes; 1:No; / 2: Swith to UTI; Yes(over / Load 1minsto restart,after over Load three times to stop / output)	Writable	1	1	1	1	20	Grid Volt	vgrid	Grid Volt AC input Volt (0,1 V)	2343	2352	0	0
21			OverTempRestart 0:Yes; / 1:No; Yes(over Temperature / To after restart，over Temperature three times to / stop output)	Writable	0	0	0	0	21			Line Freq AC input frequency	4997	4994	0	0
22			Buzzer on/off enable 1:Enable; / 0:Disable;	Writable	1	1	1	1	22			OutputVolt AC output Volt	2300	2300	2300	2300
23			Serial No 5	Writable	23122	23122	23122	23122	23			OutputFreq AC output frequency	5001	4999	4999	5000
24			Serial No 4	Writable	19248	19248	19248	19248	24			Ouput DCV Ouput DC Volt ??? probably for drycontact	0	0	0	0
25			Serial No 3				17227	17227	25	InvTemp	inverterTemperature	InvTemp Inv Temperature 0.1C			194	198
26			Serial No 2	Writable	14384	14384	14384	14384	26			DcDc Temp 0.1C	120	94	160	167
27			Serial No 1	Writable	13113	13113	13113	13113	27			LoadPercent 0-1000 0.1%	2	2	0	108
28			InverterModule High	Writable	0	0	0	0	28			Battery-port volt (DSP)	0	0	0	0
29			InverterModule Low Byte P-battery type: 0: Lead_Acid; / 1: Lithium; 2: CustomLead_Acid; / U-user type:0: No verndor; / 1: Growatt; 2: CPS; 3: Haiti; / M-power rate: 3: 3KW; 5:5KW; / S-Aging; 0: Normal Mode; / 1: Aging Mode; Can be set at / standy state Only	Writable	50	50	50	50	29			Battery-bus volt (DSP)	0	0	0	0
30			Communicate addre / Ss 1~254	Writable	1	1	1	1	30			Time total H Work time total (high)	0	0	0	0
31			FlashStart Update firmware 0x0001: own=dec1 / 0X0100: control broad (0x0100 = dec256)	Writable	256	256	256	256	31			Time total L Work time total (low)	0	0	0	0
32			Reset User Info 0x0001	Writable	0	0	0	0	32			Buck1_NTC Buck1 Temperature 0.1C	91	87	125	175
33			Reset to factory 0x0001	Writable	0	0	0	0	33			Buck2_NTC	111	77	137	147
34			MaxChargeCurr Ampere	Writable	80	80	80	80	34			OP_Curr Output Current 0.1A	6	3	5	23
35			Bulk Charge Volt (0.1V)	Writable	570	570	570	570	35			Inv_Curr Inv Current 0.1A	15	15	15	24
36			FloatChargeVolt (0.1V)	Writable	570	570	570	570	36	AC_InWatt H	pImport	AC_InWatt H	0	0	0	0
37			BatLowToUtiVolt Bat Low Volt Switch To Uti (0.1V)	Writable	300	300	300	300	37	AC_InWatt L	pImport	AC_InWatt L	0	0	0	0
38			ACChargeCurr (1A)	Writable	20	20	20	20	38			AC_InVA H	0	0	0	0
39			Battery Type 0: AGM 1: FLD / 2: USE 3: Lithium; 4: USE2 Can be set at standy state / Only	Writable	3	3	3	3	39			AC_InVA L	0	0	0	0
40			Aging Mode 0: Normal Mode; / 1: Aging Mode; Can be set at / standy state Only	Writable	0	0	0	0	40	Fault bit	inverterError	Fault bit:2 Over Temperature / 3 Bat Voltage High / 5 Output short / 6 Output voltage high / 7 Over Load / 8 Bus voltage high / 9 Bus start fail / 51 over current / 52 Bus voltage low / 53 inverter softstart fail / 56 battery open / 58 output voltage low / 60 negtive power / 61 PV voltage high / PV62 SCI com error / 80 can fault Can / 81 host loss	0	0	0	0
41				Writable	0	0	0	0	41			Warning bit see 40	0	0	0	0
42			Safety Type 1 standard 2 ETL / 3 AS4777 4 CQC 5 VDE4105	Writable	1	1	1	1	42			Warning bit high	0	0	0	0
43			DTC Device Type Code (Inverter)	Writable	20105	20105	20105	20105	43			warning value	0	0	0	0
44			??????????		0	0	0	0	44			Device Type Code &*6	20105	20105	20105	20105
45			System time-year		2024	2024	2024	2024	45			Product check step ??? looks like Grid Volt reg 20	2383	2356	0	0
46			System time- Month		1	1	11	12	46			Production Line Mode 0: Not at Production / Line Mode; / 1: Production Line / Mode; / 2: Production Line / Clear Fault Mode;	0	0	0	0
47			System time- Day		16	17	28	1	47	ConstantPowerOKFlag	constantpowerok	ConstantPowerOKFlag 0: Not OK; / 1: OK; ?? refers to constant from pv? Would be interesting	0	0	0	0
48			System time- Hour		19	14	19	15	48	Epv1_today H	epvToday	Epv1_today H PV Energy today 0.1kwh	0	0	0	0
49			System time- Min		37	23	31	6	49	Epv1_today L	epvToday	Epv1_today L	0	0	0	58
50			System time- Second		58	26	54	11	50	Epv1_total H	epvTotal	Epv1_total H PV Energy total	0	0	0	0
51			??????????		0	0	0	0	51	Epv1_total L	epvTotal	Epv1_total L PV Energy total	2453	2453	13932	14072
52			??????????		0	0	0	0	52	Epv2_today H	epvToday	Epv2_today H	0	0	0	0
53			??????????		0	0	0	0	53	Epv2_today L	epvToday	Epv2_today L	0	0	0	0
54			??????????		0	0	0	0	54	Epv2_total H	epvTotal	Epv2_total H PV Energy total	0	0	0	0
55			??????????		0	0	0	0	55	Epv2_total L	epvTotal	Epv2_total L PV Energy total	0	0	0	0
56			??????????		0	0	0	0	56	Eac_chrToday H	eImportToday	Eac_chrToday H AC charge Energy today	0	0	0	0
57			??????????		0	0	0	0	57	Eac_chrToday L	eImportToday	Eac_chrToday L	0	0	0	0
58			??????????		0	0	0	0	58	Eac_chrTotal H	eImportTotal	Eac_chrTotal H AC charge Energy total	0	0	0	0
59			Manufacturer Info 8 high ASCII		0	0	0	0	59	Eac_chrTotal L	eImportTotal	Eac_chrTotal L AC charge Energy total 0.1kwh	168	168	1034	1034
60			Manufacturer Info 7 middle		0	0	0	0	60	Ebat_dischrToday H	eDischargeToday	Ebat_dischrToday H Bat discharge Energy today 0.1kwh	0	0	0	0
61			Manufacturer Info 6 low		0	0	0	0	61	Ebat_dischrToday L	eDischargeToday	Ebat_dischrToday L	0	0	0	3
62			Manufacturer Info 5 high		0	0	0	0	62	Ebat_dischrTotal H	eDischargeTotal	Ebat_dischrTotal H Bat discharge Energy total 0.1kwh	0	0	0	0
63			Manufacturer Info 4 middle		0	0	0	0	63	Ebat_dischrTotal L	eDischargeTotal	Ebat_dischrTotal L	845	845	5461	5496
64			Manufacturer Info 3 low		0	0	0	0	64	Eac_dischrToday H	eLoadToday	Eac_dischrToday H AC discharge Energy today	0	0	0	0
65			Manufacturer Info 2 high		0	0	0	0	65	Eac_dischrToday L	eLoadToday	Eac_dischrToday L	0	0	0	0
66			Manufacturer Info 1 low		0	0	0	0	66	Eac_dischrTotal H	eLoadTotal	Eac_dischrTotal H AC discharge Energy total	0	0	0	0
67			FW Build No. 4Control FW Build No. / 2		0	0	0	0	67	Eac_dischrTotal L	eLoadTotal	Eac_dischrTotal L (only from Grid without pv)	92	92	1366	1366
68			FW Build No. 3Control FW Build No. / 1		0	0	0	0	68			ACChrCurr AC Charge Battery Current 0.1A	0	0	0	0
69			FW Build No. 2COM FW Build No. 2		0	0	0	0	69	AC_DisChrWatt H	pExport	AC_DisChrWatt H AC discharge watt (high) see Reg 9	0	0	65535	0
70			FW Build No. 1COM FW Build No. 1		0	0	0	0	70	AC_DisChrWatt L	pExport	AC_DisChrWatt L see Reg 10	100	110	65516	5150
71			??????????		0	0	0	0	71	AC_DisChrVA H	pLoad	AC_DisChrVA H see Reg 11 ()from Battery + from Sun + from Grid now	0	0	0	0
72			Sys Weekly 0-6 ???		0	0	0	0	72	AC_DisChrVA L	pLoad	AC_DisChrVA L see Reg 12	1400	890	1280	5390
73			ModbusVersion		0	0	0	0	73	Bat_DisChrWatt H	pDischarge	Bat_DisChrWatt H 0.1W Battery discharge power	0	0	0	0
74					65535	65535	65535	65535	74	Bat_DisChrWatt L	pDischarge	Bat_DisChrWatt L Battery discharge power	0	0	210	2430
75					0	0	0	0	75			Bat_DisChrVA H 0.1VA Bat discharge apparent power / (high)	0	0	0	0
76			Rate active / power(high) W		0	0	0	0	76			Bat_DisChrVA L Bat discharge apparent power / (low)	0	0	210	2480
77			Rate active / power(low) (0.1W) W		50000	50000	50000	50000	77	Bat_Watt H	pCharge	Bat_Watt H ?? (signed int 32) / Positive:Battery / Discharge Power; / Negative: / Battery / Charge Power;	0	65535	0	0
78			Rate apparent power / (high) VA		0	0	0	0	78	Bat_Watt L	pCharge	Bat_Watt L ???	0	63956	210	2480
79			Rate apparent power / (low) (0.1VA) VA		50000	50000	50000	50000	79			UwSlaveExistCnt ???	0	0	0	0
80			Communicaiton / board Version For BMS / Board		5603	5603	5603	5603	80			BatOverCharge 0:Battery not over / charge; / 1:Battery over charge;	0	0	0	0
81			UwBatPieceNum ???		420	420	420	420	81			MpptFanSpeed Fan speed of MPPT Charger 0-100 1%	0	0	0	0
82			WBatLowCutOff (0.1V Li: 5-100 %)		200	200	200	200	82			InvFanSpeed Fan speed of Inverter 0-100%	21	25	20	31
83			??????????		2300	2300	2300	2300	83			TotalChgCur Total Charge current 0.1A see also Reg No. 7	0	29	0	0
84			NomGridVolt		2300	2300	2300	2300	84			????	0	0	4	47
85			NomGridFreq		500	500	500	500	85	Eop_dischrToday_H	eExportToday	Eop_dischrToday_H Op discharge Enerday today	0	0	0	0
86			NomBatVolt		480	480	480	480	86	Eop_dischrToday_L	eExportToday	Eop_dischrToday_L	0	0	0	23
87			NomPvCurr		600	600	600	600	87	Eop_dischrTotal_H	eExportTotal	Eop_dischrTotal_H Op discharge Enerday total	0	0	0	0
88			NomAcChgCurr		300	300	300	300	88	Eop_dischrTotal_L	eExportTotal	Eop_dischrTotal_L	0	0	0	69
89			NomOpVolt		2300	2300	2300	2300	89			?????	0	0	0	0
90			NomOpFreq		500	500	500	500	90			ParaChgCurr Para system charge current
91			NomOpPow		5000	5000	5000	5000
92			??????????		4	4	4	4
93			??????????		20	20	20	20
94			??????????		420	420	420	420
95			uwAC2BatVolt AC switch to Battery 01%		500	500	390	390
96			BypEnable		0	0	0	0
97			PowSavingEn		0	0	0	0
98			SpowBalEn		1	1	1	1
99			ClrEnergyToday???		0	0	0	0
100			clrEnergyAll???		0	0	0	0
101			BurnInTestEn??		0	0	0	0
102			ManualStartEn??		0	0	0	0
103			SciLossChkEn??		0	0	0	0
104			BlightEn		1	1	1	1
105			ParaMaxChgCurr	Parallel / Maximum / Current System / Charge	80	80	80	80
106			LiProtocolType	1-99	51	51	51	51
107			AudioAlarmEn		1	1	1	1
108			uwEqEn?		0	0	0	0
109			uwEqChgVolt??		2	12	2	12
110			uwEqTime??		0	2589	0	1352
111			uwEqTimeOut??		0	0	0	0
112			uwEqInterval		0	0	0	0
113			uwMaxDisChgCu / Rr (probably 0.001A Current from Utility)?? compare with Input 04		0	1640	0	2990
114			??????????		0	0	0	0
115			??????????		0	0	0	0
116			??????????		0	31	0	56
117			??????????		0	0	0	0
118			??????????		0	0	0	0
119			See 70 inputreg		100	110	0	5110
120			??????????		0	0	0	0
121			See 72 inputreg		1400	890	1150	5390
122			??????????		0	0	0	0
123			??????????		0	0	0	0
124			??????????		0	0	0	0
125			??????????		0	0	0	0
126			Battery Voltage		5232	5275	5320	5297
127			Battery Percent %		48	50	76	97
128					4143	4272	4213	4180
129			Uti Voltage now???		2343	2352	0	0
130					4997	4994	0	0
131					2300	2300	2300	2300
132					5001	4999	4999	5000
133					0	0	0	0
134					160	119	194	198
135					120	94	160	167
136					2	2	0	108
137					0	0	0	0
138					0	0	0	0
139					0	0	0	0
140					0	0	0	0
141					91	87	125	175
142					111	77	137	147
143					6	3	5	23
144					15	15	15	24
145					0	0	0	0
146					0	0	0	0
147					0	0	0	0
148					0	0	0	0
149					0	0	0	0
150					0	0	0	0
151					0	0	0	0
152					0	0	0	0
153					20105	20105	20105	20105
154					2383	2356	0	0
155					0	0	0	0
156					0	0	0	0
157					0	0	0	0
158					0	0	0	58
159					0	0	0	0
160			Total Kwh from PV		2453	2453	13932	14072
161					0	0	0	0
162			Boot loader version2		???	???	0	0

## Tabelle2
0	0
1	0
2	0
3	0
4	0
5	16
6	0
7	0
8	1
9	12342
10	14126
11	17972
12	12342
13	14382
14	17972
15	0
16	0
17	0
18	1
19	0
20	1
21	0
22	1
23	23122
24	19248
0	14384
1	13113
2	0
3	50
4	1
5	256
6	0
7	0
8	80
9	570
10	570
11	300
12	20
13	3
14	0
15	0
16	1
17	20105
18	0
19	2024
20	1
21	17
22	14
23	23
24	26
0	0
1	0
2	0
3	0
4	0
5	0
6	0
7	0
8	0
9	0
10	0
11	0
12	0
13	0
14	0
15	0
16	0
17	0
18	0
19	0
20	0
21	0
22	0
23	65535
24	0
0	0
1	50000
2	0
3	50000
4	5603
5	420
6	200
7	2300
8	2300
9	500
10	480
11	600
12	300
13	2300
14	500
15	5000
16	4
17	20
18	420
19	500
20	0
21	0
22	1
23	0
24	0
0	0
1	0
2	0
3	1
4	80
5	51
6	1
7	0
8	12
9	2589
10	0
11	0
12	1640
13	0
14	0
15	31
16	0
17	0
18	110
19	0
20	890
21	0
22	0
23	0
24	0
0	5275
1	50
2	4272
3	2352
4	4994
5	2300
6	4999
7	0
8	119
9	94
10	2
11	0
12	0
13	0
14	0
15	87
16	77
17	3
18	15
19	0
20	0
21	0
22	0
23	0
24	0
0	0
1	0
2	20105
3	2356
4	0
5	0
6	0
7	0
8	0
9	2453
10	0
11	0
Input	Registers	0-25
0	12
1	2589
2	0
3	0
4	1640
5	0
6	0
7	31
8	0
9	0
10	110
11	0
12	890
13	0
14	0
15	0
16	0
17	5275
18	50
19	4272
20	2352
21	4994
22	2300
23	4999
24	0
0	94
1	2
2	0
3	0
4	0
5	0
6	87
7	77
8	3
9	15
10	0
11	0
12	0
13	0
14	0
15	0
16	0
17	0
18	20105
19	2356
20	0
21	0
22	0
23	0
24	0
0	2453
1	0
2	0
3	0
4	0
5	0
6	0
7	0
8	168
9	0
10	0
11	0
12	845
13	0
14	0
15	0
16	92
17	0
18	0
19	110
20	0
21	890
22	0
23	0
24	0
0	0
1	65535
2	63956
3	0
4	0
5	0
6	25
7	29
8	0
9	0
10	0
11	0
12	0
13	0
End

## LegendColor
Colors Legend

	In Code used Input Registry